## Introduction
[Insert photograph of front of building]
Air Conditioning Inspection Report (Level 4)
FOR
Property | [Property]
Client | [Client]
Date of Inspection | [Date]
Report Prepared by: | [Name]
Signature | [Signature]
Contents
1) Introduction
2) Cooling Calculation
3) Sub Systems
4) Chiller
5) Heat Rejection
6) AHU's
7) Pumps
8) Packaged Units
9) Terminal Units
10) Controls BMS
11) Recommendations
Appendix A - Specific Fan Power
Appendix B - Photos
Appendix C - Refrigerant Information
Appendix D - Cooling Benchmarks
Introduction
On 4 January 2003 the European Parliament and the Council of the European Union published Directive 2002/91/EC on the Energy Performance of Buildings (EPBD). This requires Member States to bring into force 'the necessary laws, regulations and administrative provisions to comply with the Directive'. Article 9 requires Member States to introduce measures to establish a regular inspection of air conditioning systems.
To minimise the impact of the introduction of this requirement, the first such inspections will apply to systems with a capacity of over 250kW and must be completed by 4th January 2009. The remaining systems over 12kW must have the first inspections completed by 4th January 2011.
New systems brought into use after January 2008 will not require inspection until they have been in use for a maximum of 5 years.
These inspections may only be completed by an accredited Air Conditioning System Energy Assessor (ACSEA).
The EPBD Regulations define an 'air conditioning system' as: a combination of all the components required to provide a form of air treatment in which the temperature is controlled or can be lowered and includes systems which combine such air treatment with the control of ventilation, humidity and air cleanliness.
The rated cooling output of an air conditioning system could exceed 12kW where a number of individual units of less than 12kW rated cooling load output are installed to provide distributed cooling within the building under the operators demise, irrespective of whether or not the individual units are linked to a common control system. Low capacity packaged units such as 'through the wall' units may therefore need to be assessed where the total cooling capacity in the building exceeds 12kW.
The assessor/consultant shall not be liable for any use of this report and the contents within, beyond the purposes for which the report was originally prepared.
Scope of the inspection required by the EPBD Regulations
The primary aim of the inspection is to give building owners and operators information about the performance of their buildings and plant, and to identify opportunities to save energy and cut operating costs.
The Inspection and Report were undertaken in accordance with CIBSE's methodology, Inspection of Air Conditioning Systems TM44: 2012 by an inspector accredited to the National Occupational Standard and accredited by CIBSE Certification.
The inspection is as far as possible carried out by making visual observations of representative sample of the air conditioning equipment and other visual indicators such as refrigerant sight glasses, pressure, temperature or filter gauges, although where these are not available the inspector may have taken some test readings. The inspection also included an examination of records of design, construction and maintenance where made available.
The inspector is also required to estimate whether the system is suitably sized for the cooling loads in the treated spaces, and to provide advice on ways in which improvement might be made.
Health and Safety Issues
Inspectors have a duty to comply with relevant health and safety legislation. This includes a duty to draw the building owner or managers attention to obvious instances of inadequate maintenance or neglect, where these might have implications for the health and safety of building occupants or the public.
Building
Organisation Name |  | [Enter]
Building Manager |  | [Enter]
Street Address (UPRN) |  | [Enter]
Postcode
Building Occupier
Organisation Name |  | [Enter]
Street Address (UPRN) |  | [Enter]
Postcode
Accredited Inspector Details
Inspector Name |  | [Enter] | Accreditation Scheme |  | CIBSE Certification
Inspector Number |  | CACI[Enter 6 digits]
Company Name |  | [Enter]
Address |  | [Enter]
[Enter]
[Enter]
Postcode |  | [Enter]
Scope of Inspection
Scope |  | [Enter] | Date of Inspection |  | [Enter]
Report Issued |  | [Enter] | Valid until |  | [Enter]
Executive Summary
System Description
[ACI to fully describe the building AC equipment]
Inspection Observations
[ACI to list the inspection observations]
Recommendations Summary (refer to "Recommendation" section for further details)
[ACI to list the recommendations]
Alternative Solutions (refer to TM44 section 5)
[ACI to list the alternative solutions]
Record Checklist Pre Inspection Information
Level |  | Information Required |  | Source |  | Not Available
Essential | Itemised list of installed air conditioning and refrigeration plant including product makes, models and identification numbers. |  |  | [Enter source of information] |  | [If not available, provide reason]
Cooling capacities, with locations of the indoor and outdoor components of each plant.
Description of system control zones, with schematic drawings.
Description of method of control of temperature.
Description of method of control of periods of operation.
Floor plans and schematics of air conditioning systems.
Area in meters square of conditioned space
Desirable | A previously completed Building logbook (based on TM31) for new and sometimes existing buildings |  |  | [Enter source of information] |  | [If not available, provide reason]
Reports from earlier inspections of air conditioning systems, and for the generation of an energy performance certificate.
Records of maintenance operations carried out on refrigeration systems, including cleaning indoor and outdoor heat exchangers, refrigerant leakage tests, repairs to refrigeration components or replenishing with refrigerant.
Records of maintenance operations carried out on air delivery systems, including filter cleaning and changing, and cleaning of heat exchangers.
Records of calibration and maintenance operations carried out on control systems and sensors, or BMS systems and sensors.
Records of sub-metered air conditioning plant use or energy consumption.
For relevant air supply and extract systems, commissioning results of measured absorbed power at normal air delivery and extract rates, and commissioning results for normal delivered delivery and extract air flow rates (or independently calculated specific fan power for the system).
Optional | An estimate of the design cooling load for each system (if available). Otherwise, a brief description of the occupation of the cooled spaces, and of power consuming equipment normally used in those spaces. |  |  | [Enter source of information] |  | [If not available, provide reason]
Records of any issues or complaints that have been raised concerning the indoor comfort conditions achieved in the treated spaces.
Where a BMS is used the manager should arrange for a short statement to be provided describing its capabilities, the plant it is connected to control, the set points for the control of temperature, the frequency with which it is maintained, and the date of the last inspection and maintenance.
Where a monitoring station, or remote monitoring facility, is used to continually observe the performance of equipment such as chillers, the manager should arrange for a statement to be provided describing the parameters monitored, and a statement reviewing the operating efficiency of the equipment.

## Cooling Calculation
Cooling plant calculation
Inspection Notes
Item | Guidance Notes | Inspection Notes |  |  | Comments
Appropriately sized cooling plant | Compare system sizes with likely loads. Section 4 TM44 contains simple procedures for assessing whether refrigeration systems and air supply systems are likely to be oversized |  |  |  | [Comment on size of the cooling plant]
|  | Total Occupants | 0
|  | Floor Area | 0 | m²
|  | Occupant Density/m² | #DIV/0! | m²
| The installed cooling capacity should consider the capacity of all cooling plant taking into account the resilience strategy. For example, 3x5kW split DX units operating in the building has an installed capacity of 15kW | Installed cooling capacity | 0 | kW
|  | This equates to a capacity of | #DIV/0! | Watts/m² | [Compare capacity of inspection results to Appendix C for cooling benchmarks]
|  | Benchmark cooling capacity |  | Watts/m²
(see appendix C for advice)
The installed size is deemed
Acceptable
Unacceptable

## Sub Systems
Sub-systems
Volume Definitions | [Enter]
Sub System ID | [Enter]
Sub System Description | [Enter]
Effective Rated Cooling Output of the Sub System (kW) | [Enter]
Sub System Area Served | [Enter]
Inspection Date | [Enter]
Cooling Plant Count | [Enter]
AHU Count | [Enter]
Terminal Units Count | [Enter]
Sub System Controls Count | [Enter]

## Chiller
Chiller Plant Equipment |  | Note: For multiple chillers within the same system copy this worksheet and fill it in for each individual chiller. Verify information provided by client is correct by way of inspection and insert actual information below (see TM44 section 3.2.1).
System Identifier |  | [Enter]
Manufacturer |  | [Enter]
Description |  | [Enter]
Model/Reference |  | [Enter]
Serial Number's |  | [Enter]
Year Plant Installed |  | [Enter]
Rated Cooling Capacity (kW) |  | [Enter]
Refrigerant Type For more info see appendix C |  | [Enter] | What is the status of this refrigerant? (e.g. banned, being phased out or Legal) |  |  |  | [Enter]
Location |  | [Enter]
Areas / Systems Served |  | [Enter]
Noted discrepancies between information provided and on site information collected |  | [Enter]
Chiller Plant Equipment Visual Inspection | [8 empty] | Comments
Is Chiller operational? |  |  | Yes | No |  |  |  |  | [Comment]
Is area around chiller clear of obstructions and debris? |  |  | Yes | No |  |  |  |  | [Comment]
Is the general condition of chiller and associated central plant in good order? |  |  | Yes | No |  |  |  |  | [Comment]
Assess temperature difference/ and observe refrigerant via sight glass or pressure gauge. Suitable? |  |  | Yes | No |  |  |  |  | [Comment]
Does area around plant show signs of oily stains indicative of a refrigerant leak? |  |  | Yes | No |  |  |  |  | [Comment]
Is insulation on primary circulation pipe work, well fitted and in good condition? |  |  | Yes | No |  |  |  |  | [Comment]
Is the chiller unit placed clear from warm air discharge louvres? |  |  | Yes | No |  |  |  |  | [Comment]
Locate the compressors and ensure that they are operational or can be brought into operation. |  |  | Yes | No |  |  |  |  | [Comment]
Are there any energy efficiency measures evident in the system design? e.g. free cooling (separate coil or compressor by pass), connection to ground water, heat recovery of condenser water |  |  | Yes | No |  |  |  |  | [Comment]
Chiller Plant Inspection
Inspection Notes
Item | Guidance Notes |  | Inspection Notes | [5 empty] | Comments
Appropriately sized cooling plant | Compare system sizes with likely loads. Section 4 TM44 contains simple procedures for assessing whether refrigeration systems and air supply systems are likely to be oversized | [7 empty] | [Comment on size of chiller]
Total Occupants
|  |  | Floor Area |  |  |  | m²
|  |  | Occupant Density/M2 |  |  |  | m²
| The installed cooling capacity should consider the capacity of all chiller plant taking into account the resilience strategy. For example, 3x100kW chillers operating with 1 on standby has an installed capacity of 200kW |  | Installed cooling capacity |  |  |  | kW
|  |  | This equates to a capacity of |  |  |  | Watts/m² |  | [Compare capacity of inspection results to Appendix D for cooling benchmarks]
|  |  | Benchmark cooling capacity |  |  |  | Watts/m²
(see appendix D for advice)
The installed size is deemed
Acceptable
Unacceptable
Refrigerant used | Identify the refrigerant used |  | Refrigerant name | [Enter] |  |  |  |  | [Comment]
|  |  | What is the weight of the refrigerant? |  |  |  |  | kg
F gas refrigerant requiring regular leakage inspection
| Indicate whether system is compliant with F Gas Regulation inspections |  | Yes | No
|  |  | Has inspection been carried out as required | [5 empty] | [Comment]
|  |  | Yes | No
|  |  | Date of Last inspection | [5 empty] | [Comment]
Refrigeration Charge | Sight glass inspection. Describe what can be seen and possible reason. For example "air in refrigerant, system may be undercharged or there is a leak" |  | Comment on the view through the refrigerant sight glass
[Enter]
If you have the equipment, measure the temperature difference across the refrigeration compressor and compare condenser temperature with the ambient temperature in the plant room/outside air. If the temperature lift from the compressor is excessive the chiller COP will be reduced.
|  |  | Ambient Temperature |  |  |  | ˚C |  | [comment on the temperatures]
|  |  | Pre compressor |  |  |  | ˚C
|  |  | Post compressor |  |  |  | ˚C
|  |  | The temperature is deemed: |  | Acceptable
Unacceptable
Compressor Oil | Comment on the compressor oil level, check for leaks and describe what can be seen through the site glass |  | [Enter]
Refrigeration Leaks | Note whether refrigeration heat exchangers show signs of oily staining that could indicate refrigerant leakage. If present, check whether any attention to this is noted in the maintenance records. |  | Are there any signs of a refrigerant leak? | [5 empty] | [Comment]
|  |  | Yes | No
Operation | Record and comment on operational parameters for the cooling plant. |  | Record design CHW system | [5 empty] | [Comment]
|  |  | Flow | ˚C Return |  | ˚C
|  |  | The chiller setpoints reported at service( ) were as follows: | [5 empty] | [Comment]
|  |  | Flow | ˚C Return |  | ˚C
|  |  | Chiller setpoints observed during the inspection were: | [5 empty] | [Comment]
|  |  | Flow | ˚C Return |  | ˚C
Regular Maintenance | Record whether there is evidence of a regular inspection and maintenance regime carried out by suitably competent people. Record and comment on the frequencies and scope of maintenance to the air conditioning equipment and systems in relation to industry |  | Are there records of regular maintenance? | [5 empty] | [Comment]
|  |  | Yes | No
|  |  | Is the maintenance undertaken by suitably competent people? | [5 empty] | [Comment]
|  |  | Yes | No
|  |  | Are frequency of maintenance visits adequate and in line with industry guidelines? | [5 empty] | [Comment]
|  |  | Yes | No
|  |  | Dates of most recent maintenance visits | [5 empty] | [Comment]
Metering | Is metering installed to enable monitoring of energy consumption of refrigeration plant? | [7 empty] | [Comment]
|  |  | Yes | No
[Comment]
| Is a BEMs installed in the building which can warn of out of range values? |  | Yes | No

## Heat Rejection
Heat Rejection Plant Equipment |  | Note: For multiple plant within the same system copy this worksheet and fill it in for each individual unit. Verify information provided by client is correct by way of inspection and insert actual information below (see TM44 section 3.2.1).
System Identifier |  | [Enter]
Manufacturer |  | [Enter]
Description I.e. Integral to Air cooled chiller, Dry air cooler, cooling tower |  | [Enter]
Model/Reference |  | [Enter]
Serial Number |  | [Enter]
Year Plant Installed |  | [Enter]
Rated Capacity (kW) where possible give ambient condition for rating |  | [Enter] @ [Enter]°C ambient
Location |  | [Enter]
Areas / Systems Served |  | [Enter]
Noted discrepancies between information provided and on site information collected |  | [Enter]
Heat Rejection Plant Visual Inspection | [5 empty] | Comments
Is heat rejection plant operational? |  |  | Yes | No |  | [Comment]
Is area around heat rejection plant clear of obstructions and debris? |  |  | Yes | No |  | [Comment]
Is there any possibility of air recirculation through the device? |  |  | Yes | No |  | [Comment]
Is the general condition of plant in good order? |  |  | Yes | No |  | [Comment]
If present, are heat exchangers undamaged/un-corroded and clean? |  |  | Yes | No |  | [Comment]
Does area around plant show signs of leakage? |  |  | Yes | No |  | [Comment]
Is insulation on pipe work, where required, well fitted and in good condition? |  |  | Yes | No |  | [Comment]
Is the heat rejection placed clear from other equipment it could affect such as AHU intakes? |  |  | Yes | No |  | [Comment]
Heat Rejection Equipment
Inspection Notes
Item | Guidance Notes |  | Inspection Notes |  |  | Comments
Operation | Record and comment on operational parameters for the cooling plant. |  | Record design peak ambient temperature |  |  | [Comment on the temperatures]
°C
Record design peak condenser temperature
°C
Record ambient temperature at inspection
°C
Record condenser temperature at inspection
°C
When the ambient temperature is low the heat rejection plant can often work with lower condenser temperatures to improve chiller efficiency
Do temperatures suggest that heat rejection plant is operating with optimum efficiency?
[Enter]
Regular Maintenance | Record whether there is evidence of a regular inspection and maintenance regime carried out by suitably competent people. Record and comment on the frequencies and scope of maintenance to the air conditioning equipment and systems in relation to industry guidance. |  | Are there records of regular maintenance? |  |  | [Comment]
|  |  | Yes | No
Is the maintenance undertaken by suitably competent people?
|  |  | Yes | No
[Comment]
Are frequency of maintenance visits adequate and in line with industry guidelines?
|  |  | Yes | No |  | [Comment]
Dates of most recent maintenance visits
[Enter]
Metering | Is metering installed to enable monitoring of energy consumption of heat rejection equipment? |  |  |  |  | [Comment]
|  |  | Yes | No
[Comment]
| Is a BEMS installed in the building which can warn of out of range values? |  | Yes | No
Pump Condition | Visually check the condition and operation of pumps and ancillary equipment
|  |  | Are the Condenser water pumps in good working order? |  |  | [Provide comment on the condition]
|  |  | Yes | No
|  |  | Are the Condenser water pumps inverter driven? |  |  | [Comment]
|  |  | Yes | No
Operation | Establish the operation of the pumps and drives |  | How are the pumps controlled |  |  | [Comment]
[Enter]
Provide comment regarding operation

## AHU's
Air Handling Systems Equipment
System Identifier |  | [Enter]
Serial no. |  | [Enter]
Systems served from air handling plant |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
location |  | [Enter]
Areas / Systems served |  | [Enter]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes |  |  |  | Comments
Filters | Check condition of intake air filters and check air inlets and outlets for obstruction. | [5 empty] | [Comment]
Inlet and filter conditions acceptable
|  |  | Yes | No
| Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. |  | Filter Changing Frequency:
The frequency is deemed:
Acceptable
Unacceptable
Specific Fan Power | Estimate the specific fan power (SFP) of air movement systems, provided that this can be done simply from existing records of the installed fan capacities and the flow rates and pressure drops noted in commissioning records for comparison with the industry guidance | [5 empty] | [Comment]
Are air flow rates and system pressures available from commissioning data?
|  |  | Yes | No
|  |  | Calculated SPF |  | W/(litre/s)
Condition of Heat exchangers | Assess condition of heat exchangers, Note whether any heat exchanger surfaces are significantly damaged or blocked by debris or dust. Where reasonably practical and where suitable information is available for comparison, the air path resistance across the coil should be measured. | [5 empty] | [Comment]
Are heat exchangers in good condition?
|  |  | Yes | No
If no provide description below:
[Enter]
Refrigeration leaks | Note whether refrigeration heat exchangers show signs of oily staining that could indicate refrigerant leakage. If present check whether any attention to this is noted in the maintenance records.
|  |  | Are there any signs of a refrigerant leak? |  |  |  | [Comment]
|  |  | Yes | No |  | n/a
If Yes provide comment regarding the incident and how it has been rectified:
[Enter]
Fan & Control | Note the fan type and method of speed control. |  | Are the fans provided with speed control? |  |  |  | [Comment]
|  |  | Yes | No
Fan type:
Heat recovery | Identify if the systems have any energy conservation facilities, e.g. heat recovery, free cooling sequence, and check for evidence that such facilities are/have been functioning. |  | Are energy conservation facilities installed? |  |  |  | [Comment]
|  |  | Yes | No
Identify measures installed:
[Enter]
Air Leakage | Observe the air handling plant and visible air containment including ductwork, floor or ceiling plenums and builders work shafts for signs of excessive leakage and energy loss. |  | Are there signs of excessive leakage from duct systems |  |  |  | [Comment]
|  |  | Yes | No
If Yes provide comment :
[Enter]
Outdoor air inlets | a) Locate the inlets for outdoor air. | [5 empty] | [Comment]
| b) Note any significant obstructions or blockages to inlet grilles, screens and pre-filters. |  | Are air inlets, screens or pre filters subject to obstruction or blockages?
|  |  | Yes | No
| c) Note where inlets may be affected by proximity to local sources of heat, or to air exhausts. |  | Can air inlets be affected by close proximity to local heat sources or air exhausts? |  |  |  | [Comment]
|  |  | Yes | No
| d) Check the settings and operation of air/recirculation dampers. |  | Are air dampers operating correctly?
|  |  | Yes | No
|  |  | Are recirculation air systems installed ? |  |  |  | [Comment]
|  |  | Yes | No
Are recirculation dampers set correctly ?
|  |  | Yes | No |  | n/a
Ductwork |  |  | Is the ductwork appropriately insulated? |  |  |  | [Comment]
|  |  | Yes | No
Is the ductwork leaking air?
| You may be able to measure the temperature in the supply duct from the AHU using the plug holes that were left after commissioning Design temperature should be in the O&Ms or building log book |  | Yes | No
[Comment]
AHU supply air temperature
Does this temperature match the design temperature?
|  |  | Yes | No

## Pumps
Pumped Chilled Water System
System Identifier |  | [Enter]
Serial no. |  | [Enter]
Systems served from pump plant |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
location |  | [Enter]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes |  | Comments
Insulation | Visually inspect the route and condition of the cooling system pipe work serving local areas |  |  |  | [Comment]
Is the pipe work adequately insulated?
|  |  | Yes | No
| Check that pipe work is adequately insulated. |  | If no provide comment on the condition:
[Enter]
Leaks | Leaks are not always obvious and the water can collect far from the source of the leak |  | Are there any signs of leaks? |  | [Comment]
[Enter]
Pump Condition | Visually check the condition and operation of pumps and ancillary equipment |  |  |  | [Comment]
Are the CHW water pumps in good working order?
|  |  | Yes | No
Provide comment on the condition:
|  |  | [Enter] |  | [Comment]
Are the CHW water pumps inverter driven?
|  |  | Yes | No | [Comment]
Operation | Establish the operation of the pumps and drives |  | How are the pumps controlled |  | [Comment]
[Enter]
Provide comment regarding operation

## Terminal Units
Terminal Systems Equipment
System Identifier |  | [Enter]
Description |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
Location |  | [Enter]
Areas / Systems served |  | [Enter]
Sampled Terminals |  | Unit Ref | Location | Pipe work Insulation | Ductwork Insulation | Filter condition | Signs of leakage / condensation | Noise / Vibration | Grille / Diffuser condition | General condition
|  | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter]
Sampling Instructions
Visually inspect the route and condition of the pipe work and ductwork serving local areas. Check that it is adequately insulated. Check condition of any air filters and check for obstructions. Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. Note whether these appear to provide good distribution. Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available). Assess the positioning and geometry of air supply openings in relation to extract openings. Observe if partitioning or furniture is affecting performance. Visually check the condition and operation of indoor units. Check for signs of leakage or water condensing around terminal. For example check for signs of water damage to false ceilings. Does terminal unit appear to be operating at an appropriate noise level. If concerned take measurements and review design criteria in O&M
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes | [5 empty] | Comments
Insulation | Visually inspect the route and condition of the cooling system pipe work serving local areas. |  | Is pipe work adequately insulated? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide detail:
| Check that pipe work or ductwork (or both) is adequately insulated. |  | Is ductwork adequately insulated? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide detail:
Unit Condition | Visually check the condition and operation of indoor units. |  | Are the indoor units in good working order? | [5 empty] | [Comment]
|  |  | Yes |  | No
Filters | Check condition of FCU intake air filters and check for obstructions. | [7 empty] | [Comment]
Inlet and filter conditions acceptable?
|  |  | Yes |  | No
| Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. |  | Filter Changing Frequency |  |  |  | Months
The frequency is deemed:
Acceptable
Unacceptable
Grilles & Air Flow | Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. |  | Are diffusers/grilles clean and in good order? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide comment regarding condition:
| Note whether these appear to provide good distribution |  | [Enter]
Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available).
Diffuser Positions | Assess the positioning and geometry of air supply openings in relation to extract openings. |  | Are diffusers/grilles adequately laid out? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide comment regarding condition:
| Observe if partitioning or furniture is affecting performance. |  | [Enter]

## Packaged Units
DX Systems Equipment
System Identifier |  | [Enter]
Description |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
Location
Areas / Systems served |  | [Enter]
Visual Inspection |  |  | Inspection Notes |  |  |  | Comments
Is heat rejection plant operational? |  |  | Yes | No
Is area around heat rejection plant clear of obstructions and debris? |  |  | Yes | No |  |  | [Comment]
Is there any possibility of air recirculation through the condenser? |  |  | Yes | No |  |  | [Comment]
Is the general condition of the heat rejection plant in good order? |  |  | Yes | No |  |  | [Comment]
Are condenser heat exchangers undamaged/un-corroded and clean? |  |  | Yes | No |  |  | [Comment]
Does area around plant show signs of oily stains indicative of a refrigerant leak? |  |  | Yes | No |  |  | [Comment]
Is insulation on associated pipe work, well fitted and in good condition? |  |  | Yes | No |  |  | [Comment]
Is the heat rejection plant placed clear from warm air discharge louvres? |  |  | Yes | No |  |  | [Comment]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes |  |  |  | Comments
Refrigerant used | Identify the refrigerant used |  | Refrigerant name | [Enter] |  |  | [Comment]
F gas refrigerant requiring regular leakage inspection
| Indicate whether system is compliant with F Gas Regulation inspections |  | Yes | No
Has inspection been carried out as required
|  |  | Yes | No
|  |  | Date of Last inspection |  | [Enter]
Refrigeration Leaks | Note whether refrigeration heat exchangers show signs of oily staining that could indicate refrigerant leakage. If present, check whether any attention to this is noted in the maintenance records. |  | Are there any signs of a refrigerant leak? |  |  |  | [Comment]
|  |  | Yes | No
If yes provide comment regarding the incident and how it has been rectified?
[Enter]
Insulation | Visually inspect the route and condition of the cooling system pipe work serving local areas. |  | Is pipe work adequately insulated? |  |  |  | [Comment]
|  |  | Yes | No
If no provide detail:
[Enter]
| Check that pipe work is adequately insulated. |  | Is ductwork adequately insulated? |  |  |  | [Comment]
|  |  | Yes | No
If no provide detail:
[Enter]
Unit Condition | Visually check the condition and operation of outdoor units. |  | Are the indoor units in good working order? |  |  |  | [Comment]
|  |  | Yes | No
[Enter]
| Visually check the condition and operation of indoor units. |  | Are the indoor units in good working order? |  |  |  | [Comment]
|  |  | Yes | No
[Enter]
Filters | Check condition of air filters and check for obstructions. | [5 empty] | [Comment]
Inlet and filter conditions acceptable?
|  |  | Yes | No
| Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. |  | Filter Changing Frequency |  |  | Months
|  |  | The frequency is deemed: |  |  |  | [Comment]
Acceptable
Unacceptable
Grilles & Air Flow | Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. |  | Are diffusers/grilles clean and in good order? |  |  |  | [Comment]
|  |  | Yes | No
If no provide comment regarding condition:
| Note whether these appear to provide good distribution |  | [Enter]
Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available).
Diffuser Positions | Assess the positioning and geometry of air supply openings in relation to extract openings. |  | Are diffusers/grilles adequately laid out? |  |  |  | [Comment]
|  |  | Yes | No
If no provide comment regarding condition:
| Observe if partitioning or furniture is affecting performance. |  | [Enter]

## Controls BMS
BMS and Controls
System Identifier |  | [Enter]
Description |  | [Enter]
Systems served |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
location |  | [Enter]
Areas / Systems served |  | [Enter]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes | [6 empty] | Comments
System Control | Assess zoning in relation to factors such as local levels of internal gain, orientation and exposure to solar radiation. |  | [Enter] | [6 empty] | [comment]
| Note the current indicated weekday and time of day on controllers against the actual day and time. |  | [Enter] | [6 empty] | [comment]
| Note the set on and off periods (for weekday and weekend, if this facility is available with the timer). |  | M | T | W | Th | F | S | S | [comment on set points]
| Identify and assess zone heating and cooling temperature control sensors. |  | [Enter] | [6 empty] | [comment]
| Note whether a dead band is or can be set between heating and cooling. |  | [Enter] | [6 empty] | [comment]
| Note whether any temperature gauges are inaccurately calibrated/ broken. |  | [Enter] | [6 empty] | [comment]
| Assess the refrigeration compressor(s) and the method of refrigeration capacity control. |  | [Enter] | [6 empty] | [comment]
| Assess means of modulating or controlling air flow rate through air supply and exhaust ducts. |  | [Enter] | [6 empty] | [comment]

## Recommendations
Recommendations
Item | Guidance Notes | Item
1 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
2 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
3 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
4 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
5 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
6 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
7 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
8 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]

## Appendix A - SFP
APPENDIX A: SFP
Specific Fan Power Calculation
System Name | Supply/Extract | Supply L/sec | Extract L/sec | kW Rating
AHU supply | S | [Enter] |  | [Enter]
AHU extract | E |  | [Enter] | [Enter]
|  | 0 | 0
Greater of Supply or Extract volume |  |  | 0 |  | L/sec
Total power (including losses) |  |  |  | 0 | Watts
|  | Specific fan power = |  | #DIV/0! | W / (L/sec)
Specific Fan Power Calculation
System Name | Supply/Extract | Supply L/sec | Extract L/sec | kW Rating
AHU supply | S | [Enter] |  | [Enter]
AHU extract | E |  | [Enter] | [Enter]
|  | 0 | 0
Greater of Supply or Extract volume |  |  | 0 |  | L/sec
Total power (including losses) |  |  |  | 0 | Watts
|  | Specific fan power = |  | #DIV/0! | W / (L/sec)
Specific Fan Power Calculation
System Name | Supply/Extract | Supply L/sec | Extract L/sec | kW Rating
AHU supply | S | [Enter] |  | [Enter]
AHU extract | E |  | [Enter] | [Enter]
|  | 0 | 0
Greater of Supply or Extract volume |  |  | 0 |  | L/sec
Total power (including losses) |  |  |  | 0 | Watts
|  | Specific fan power = |  | #DIV/0! | W / (L/sec)
Specific Fan Power Calculation
System Name | Supply/Extract | Supply L/sec | Extract L/sec | kW Rating
AHU supply | S | [Enter] |  | [Enter]
AHU extract | E |  | [Enter] | [Enter]
|  | 0 | 0
Greater of Supply or Extract volume |  |  | 0 |  | L/sec
Total power (including losses) |  |  |  | 0 | Watts
|  | Specific fan power = |  | #DIV/0! | W / (L/sec)
Guidance Notes
The specific fan power has been calculated based upon the methodology identified within the Department for Communities and Local Government, Non-Domestic Heating, Cooling and Ventilation Compliance Guide. Where the total fan power is divided by the design air flow rate through the system, the design air flow being whichever is the greater of either the supply or exhaust air flow in litre/second. The data used is as identified within the O&M manuals.

## Appendix B - Photos
APPENDIX B: PHOTOS
[Insert photos] | [Insert photos]
Fig 1: | Fig 2:
[Enter] | [Enter]
[Insert photos] | [Insert photos]
Fig 3: | Fig 4:
[Enter] | [Enter]
[Insert photos] | [Insert photos]
Fig 5:
[Enter]

## Appendix C - Refrigerants
APPENDIX C: Refrigerant Types
Due to concerns over Ozone depletion CFCs have been banned
HCFCs have also been banned for use in new plants and from 31 Dec 2009 Virgin HCFCs will be banned for plant maintenance. Recycled HCFCs will be banned from 31 Dec 2014
The UK Government published and presented to Parliament on 17th November 2000 the UK’s climate change programme. The programme sets out the UK strategy for tackling climate change and includes specific measures related to the use of HFCs:
— HFCs should only be used where other safe, technically feasible, cost effective and more environmentally acceptable alternatives do not exist
— HFCs are not sustainable in the long term: the Government believes that continued technological developments will mean that HFCs may eventually be able to be replaced in the applications where they are used
— HFC emission reduction strategies should not undermine commitments to phase out ozone depleting substances under the Montreal Protocol
— HFC emissions will not be allowed to rise unchecked.
Alternative refrigerants such as hydrocarbons (HCs), CO2 and ammonia have lower global warming potential than HFCs but have other disadvantages such as high flammability or toxicity. The table below reproduced from F-gas Support summarises the refrigerant characteristics
Common Refrigerants
CFCs | HCFCs | HFCs | Other
R11 | R22 | R125 | R744 (CO2)
R12 | R403B | R134A | R717 (Ammonia)
| R408A | R404A | R290 (Propane)
| R123 | R407C | R600A (Isobutane)
R410A
R413A
R417A
Leakage testing frequency required under EC F gas Regulation

## Appendix D - Cooling Benchmarks
APPENDIX D Cooling Benchmarks
The estimate in TM44 Figure 4.1 Variation of calculated total heat gains with occupation density accounts for internal heat gains but the total cooling load may also have solar gain and ventilation loads
Therefore you can use TM44 figure 4.1 with and make a necessary allowance for solar and ventilation loads or you can use the benchmark data below from CIBSE guide F
Type of Building | Total Cooling Load W/m²
General Office | 125
Interior Zones | 75
Perimeter Zones (up to 6m)
- 65% glazing | 180
- 60% glazing | 120
Typical buildings:
- Retail | 140
- Banks | 160
- Restaurants | 220
- Hotels | 150-300
- Computer suites | 400 (approx.)
Office Type | Installed Refrigeration capacity (W/m²)
| Good Practice | Typical
Naturally Ventilated | 5 | 8
Air Conditioned Standard | 90 | 125
Air Conditioned Prestige | 100 | 135