## Introduction
[Insert photograph of front of building]
Air Conditioning Inspection Report (Level 3)
FOR
Property | [Property]
Client | [Client]
Date of Inspection | [Date]
Report Prepared by: | [Name]
Signature | [Signature]
Contents
1) Introduction
2) Cooling Calculation
3) Sub Systems
4) Terminal Units
5) Packaged Units
6) Controls
7) Recommendations
Appendix A - Specific Fan Power
Appendix B - Photos
Appendix C - Refrigerant Information
Appendix D - Cooling Benchmarks
Introduction
On 4 January 2003 the European Parliament and the Council of the European Union published Directive 2002/91/EC on the Energy Performance of Buildings (EPBD). This requires Member States to bring into force 'the necessary laws, regulations and administrative provisions to comply with the Directive'. Article 9 requires Member States to introduce measures to establish a regular inspection of air conditioning systems.
To minimise the impact of the introduction of this requirement, the first such inspections will apply to systems with a capacity of over 250kW and must be completed by 4th January 2009. The remaining systems over 12kW must have the first inspections completed by 4th January 2011.
New systems brought into use after January 2008 will not require inspection until they have been in use for a maximum of 5 years.
These inspections may only be completed by an accredited Air Conditioning System Energy Assessor (ACSEA).
The EPBD Regulations define an 'air conditioning system' as: a combination of all the components required to provide a form of air treatment in which the temperature is controlled or can be lowered and includes systems which combine such air treatment with the control of ventilation, humidity and air cleanliness.
The rated cooling output of an air conditioning system could exceed 12kW where a number of individual units of less than 12kW rated cooling load output are installed to provide distributed cooling within the building under the operators demise, irrespective of whether or not the individual units are linked to a common control system. Low capacity packaged units such as 'through the wall' units may therefore need to be assessed where the total cooling capacity in the building exceeds 12kW.
The assessor/consultant shall not be liable for any use of this report and the contents within, beyond the purposes for which the report was originally prepared.
Scope of the inspection required by the EPBD Regulations
The primary aim of the inspection is to give building owners and operators information about the performance of their buildings and plant, and to identify opportunities to save energy and cut operating costs.
The Inspection and Report were undertaken in accordance with CIBSE's methodology, Inspection of Air Conditioning Systems TM44: 2012 by an inspector accredited to the National Occupational Standard and accredited by CIBSE Certification.
The inspection is as far as possible carried out by making visual observations of representative sample of the air conditioning equipment and other visual indicators such as refrigerant sight glasses, pressure, temperature or filter gauges, although where these are not available the inspector may have taken some test readings. The inspection also included an examination of records of design, construction and maintenance where made available.
The inspector is also required to estimate whether the system is suitably sized for the cooling loads in the treated spaces, and to provide advice on ways in which improvement might be made.
Health and Safety Issues
Inspectors have a duty to comply with relevant health and safety legislation. This includes a duty to draw the building owner or managers attention to obvious instances of inadequate maintenance or neglect, where these might have implications for the health and safety of building occupants or the public.
Building
Organisation Name |  | [Enter]
Building Manager |  | [Enter]
Street Address (UPRN) |  | [Enter]
Postcode
Building Occupier
Organisation Name |  | [Enter]
Street Address (UPRN) |  | [Enter]
Postcode
Accredited Inspector Details
Inspector Name |  | [Enter] | Accreditation Scheme |  | CIBSE Certification
Inspector Number |  | CACI[Enter 6 digits]
Company Name |  | [Enter]
Address |  | [Enter]
[Enter]
[Enter]
Postcode |  | [Enter]
Scope of Inspection
Scope |  | [Enter] | Date of Inspection |  | [Enter]
Report Issued |  | [Enter] | Valid until |  | [Enter]
Executive Summary
System Description
[ACI to fully describe the building AC equipment]
Inspection Observations
[ACI to list the inspection observations]
Recommendations Summary (refer to "Recommendation" section for further details)
[ACI to list the recommendations]
Alternative Solutions (refer to TM44 section 5)
[ACI to list the alternative solutions]
Record Checklist Pre Inspection Information
Level |  | Information Required |  | Source |  | Not Available
Essential | Itemised list of installed air conditioning and refrigeration plant including product makes, models and identification numbers. |  |  | [Enter source of information] |  | [If not available, provide reason]
Cooling capacities, with locations of the indoor and outdoor components of each plant.
Description of system control zones, with schematic drawings.
Description of method of control of temperature.
Description of method of control of periods of operation.
Floor plans and schematics of air conditioning systems.
Area in meters square of conditioned space
Desirable | A previously completed Building logbook (based on TM31) for new and sometimes existing buildings |  |  | [Enter source of information] |  | [If not available, provide reason]
Reports from earlier inspections of air conditioning systems, and for the generation of an energy performance certificate.
Records of maintenance operations carried out on refrigeration systems, including cleaning indoor and outdoor heat exchangers, refrigerant leakage tests, repairs to refrigeration components or replenishing with refrigerant.
Records of maintenance operations carried out on air delivery systems, including filter cleaning and changing, and cleaning of heat exchangers.
Records of calibration and maintenance operations carried out on control systems and sensors, or BMS systems and sensors.
Records of sub-metered air conditioning plant use or energy consumption.
For relevant air supply and extract systems, commissioning results of measured absorbed power at normal air delivery and extract rates, and commissioning results for normal delivered delivery and extract air flow rates (or independently calculated specific fan power for the system).
Optional | An estimate of the design cooling load for each system (if available). Otherwise, a brief description of the occupation of the cooled spaces, and of power consuming equipment normally used in those spaces. |  |  | [Enter source of information] |  | [If not available, provide reason]
Records of any issues or complaints that have been raised concerning the indoor comfort conditions achieved in the treated spaces.
Where a BMS is used the manager should arrange for a short statement to be provided describing its capabilities, the plant it is connected to control, the set points for the control of temperature, the frequency with which it is maintained, and the date of the last inspection and maintenance.
Where a monitoring station, or remote monitoring facility, is used to continually observe the performance of equipment such as chillers, the manager should arrange for a statement to be provided describing the parameters monitored, and a statement reviewing the operating efficiency of the equipment.

## Cooling Calculation
Cooling plant calculation
Inspection Notes
Item | Guidance Notes | Inspection Notes |  |  | Comments
Appropriately sized cooling plant | Compare system sizes with likely loads. Section 4 TM44 contains simple procedures for assessing whether refrigeration systems and air supply systems are likely to be oversized |  |  |  | [Comment on size of the cooling plant]
|  | Total Occupants | 0
|  | Floor Area | 0 | m²
|  | Occupant Density/m² | #DIV/0! | m²
| The installed cooling capacity should consider the capacity of all cooling plant taking into account the resilience strategy. For example, 3x5kW split DX units operating in the building has an installed capacity of 15kW | Installed cooling capacity | 0 | kW
|  | This equates to a capacity of | #DIV/0! | Watts/m² | [Compare capacity of inspection results to Appendix C for cooling benchmarks]
|  | Benchmark cooling capacity |  | Watts/m²
(see appendix C for advice)
The installed size is deemed
Acceptable
Unacceptable

## Subsystems
Sub-systems
Volume Definitions | [Enter]
Sub System ID | [Enter]
Sub System Description | [Enter]
Effective Rated Cooling Output of the Sub System (kW) | [Enter]
Sub System Area Served | [Enter]
Inspection Date | [Enter]
Cooling Plant Count | [Enter]
AHU Count | [Enter]
Terminal Units Count | [Enter]
Sub System Controls Count | [Enter]

## Terminal Units
Terminal Systems Equipment
System Identifier |  | [Enter]
System description |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
Location |  | [Enter]
Areas / Systems served |  | [Enter]
Sampled Terminals |  | Unit Ref | Location | Pipe work Insulation | Ductwork Insulation | Filter condition | Signs of leakage / condensation | Noise / Vibration | Grille / Diffuser condition | General condition
|  | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter] | [Enter]
Sampling Instructions
Visually inspect the route and condition of the pipe work and ductwork serving local areas. Check that it is adequately insulated. Check condition of any air filters and check for obstructions. Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. Note whether these appear to provide good distribution. Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available). Assess the positioning and geometry of air supply openings in relation to extract openings. Observe if partitioning or furniture is affecting performance. Visually check the condition and operation of indoor units. Check for signs of leakage or water condensing around terminal. For example check for signs of water damage to false ceilings. Does terminal unit appear to be operating at an appropriate noise level. If concerned take measurements and review design criteria in O&M
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes | [5 empty] | Comments
Insulation | Visually inspect the route and condition of the cooling system pipe work serving local areas. |  | Is pipe work adequately insulated? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide detail:
| Check that pipe work or ductwork (or both) is adequately insulated. |  | Is ductwork adequately insulated? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide detail:
Unit Condition | Visually check the condition and operation of indoor units. |  | Are the indoor units in good working order? | [5 empty] | [Comment]
|  |  | Yes |  | No
Filters | Check condition of FCU intake air filters and check for obstructions. | [7 empty] | [Comment]
Inlet and filter conditions acceptable?
|  |  | Yes |  | No
| Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. |  | Filter Changing Frequency |  |  |  | Months
The frequency is deemed:
Acceptable
Unacceptable
Grilles & Air Flow | Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. |  | Are diffusers/grilles clean and in good order? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide comment regarding condition:
| Note whether these appear to provide good distribution |  | [Enter]
Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available).
Diffuser Positions | Assess the positioning and geometry of air supply openings in relation to extract openings. |  | Are diffusers/grilles adequately laid out? | [5 empty] | [Comment]
|  |  | Yes |  | No
If no provide comment regarding condition:
| Observe if partitioning or furniture is affecting performance. |  | [Enter]

## Packaged Units
DX Systems Equipment
System identifier |  | [Enter]
Serial no. |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
Location |  | [Enter]
Areas / Systems served |  | [Enter]
Visual Inspection |  |  | Inspection Notes |  |  |  |  | Comments
Is heat rejection plant operational? |  |  | Yes | No |  |  |  | [Comment]
Is area around heat rejection plant clear of obstructions and debris? |  |  | Yes | No |  |  |  | [Comment]
Is there any possibility of air recirculation through the condenser? |  |  | Yes | No |  |  |  | [Comment]
Is the general condition of the heat rejection plant in good order? |  |  | Yes | No |  |  |  | [Comment]
Are condenser heat exchangers undamaged/un-corroded and clean? |  |  | Yes | No |  |  |  | [Comment]
Does area around plant show signs of oily stains indicative of a refrigerant leak? |  |  | Yes | No |  |  |  | [Comment]
Is insulation on associated pipe work, well fitted and in good condition? |  |  | Yes | No |  |  |  | [Comment]
Is the heat rejection plant placed clear from warm air discharge louvres? |  |  | Yes | No |  |  |  | [Comment]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes |  |  |  |  | Comments
Refrigerant used | Identify the refrigerant used |  | Refrigerant name | [Enter] |  |  |  | [Comment]
Is refrigerant banned or being phased out?
|  |  | What is the total system weight of refrigerant? |  |  |  | kg
F gas refrigerant requiring regular leakage inspection
| Indicate whether system is compliant with F Gas Regulation inspections |  | Yes | No
Has inspection been carried out as required
|  |  | Yes | No
|  |  | Date of Last inspection |  | [Enter]
Refrigeration Leaks | Note whether refrigeration heat exchangers show signs of oily staining that could indicate refrigerant leakage. If present, check whether any attention to this is noted in the maintenance records. |  | Are there any signs of a refrigerant leak? |  |  |  |  | [Comment]
|  |  | Yes | No
If yes provide comment regarding the incident and how it has been rectified?
[Enter]
Insulation | Visually inspect the route and condition of the cooling system pipe work serving local areas. |  | Is pipe work adequately insulated? |  |  |  |  | [Comment]
|  |  | Yes | No
If no provide detail:
[Enter]
| Check that pipe work is adequately insulated. |  | Is ductwork adequately insulated? |  |  |  |  | [Comment]
|  |  | Yes | No
If no provide detail:
[Enter]
Unit Condition | Visually check the condition and operation of outdoor units. |  | Are the indoor units in good working order? |  |  |  |  | [Comment]
|  |  | Yes | No
[Enter]
Filters | Check condition of air filters and check for obstructions. | [6 empty] | [Comment]
Inlet and filter conditions acceptable?
|  |  | Yes | No
| Note the usual filter changing or cleaning frequency, and the elapsed time since the last change or clean, in relation to industry guidance. |  | Filter Changing Frequency |  |  | Months
|  |  | The frequency is deemed: |  |  |  |  | [Comment]
Acceptable
Unacceptable
Grilles & Air Flow | Review air delivery openings, grilles or diffusers, and route by which air is extracted from the spaces. |  | Are diffusers/grilles clean and in good order? |  |  |  |  | [Comment]
|  |  | Yes | No
If no provide comment regarding condition:
| Note whether these appear to provide good distribution |  | [Enter]
Review evidence that occupants find the air delivery arrangements unacceptable-for example check the complaints log (if available).
Diffuser Positions | Assess the positioning and geometry of air supply openings in relation to extract openings. |  | Are diffusers/grilles adequately laid out? |  |  |  |  | [Comment]
|  |  | Yes | No
If no provide comment regarding condition:
| Observe if partitioning or furniture is affecting performance. |  | [Enter]

## Controls
Controls
System identifier |  | [Enter]
System description |  | [Enter]
Systems served |  | [Enter]
Manufacturer |  | [Enter]
Year systems installed |  | [Enter]
Location |  | [Enter]
Areas / Systems served |  | [Enter]
Detailed Inspection Notes
Item | Guidance Notes |  | Inspection Notes | [6 empty] | Comments
System Control | Assess zoning in relation to factors such as local levels of internal gain, orientation and exposure to solar radiation. |  | [Enter] | [6 empty] | [comment]
| Note the current indicated weekday and time of day on controllers against the actual day and time. |  | [Enter] | [6 empty] | [comment]
| Note the set on and off periods (for weekday and weekend, if this facility is available with the timer). |  | M | T | W | Th | F | S | S | [comment on set points]
| Identify and assess zone heating and cooling temperature control sensors. |  | [Enter] | [6 empty] | [comment]
| Note whether a dead band is or can be set between heating and cooling. |  | [Enter] | [6 empty] | [comment]
| Note whether any temperature gauges are inaccurately calibrated/ broken. |  | [Enter] | [6 empty] | [comment]
| Assess the refrigeration compressor(s) and the method of refrigeration capacity control. |  | [Enter] | [6 empty] | [comment]

## Recommendations
Recommendations
Item | Guidance Notes | Item
1 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
2 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
3 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
4 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
5 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
6 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
7 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]
Item | Guidance Notes | Item
8 | Potential for Carbon savings | [Enter]
| Rationale | [Enter]
| Recommendations | [Enter]

## Appendix A - Photos
APPENDIX A: PHOTOS
[Insert photos] | [Insert photos]
Fig 1: [Enter] | Fig 2: [Enter]
[Insert photos] | [Insert photos]
Fig 3 [Enter] | Fig 4: [Enter]
[Insert photos] | [Insert photos]
Fig 5: [Enter]

## Appendix B - Refrigerants
APPENDIX B: Refrigerant Types
Due to concerns over Ozone depletion CFCs have been banned
HCFCs have also been banned for use in new plants and from 31 Dec 2009 Virgin HCFCs will be banned for plant maintenance. Recycled HCFCs will be banned from 31 Dec 2014
The UK Government published and presented to Parliament on 17th November 2000 the UK’s climate change programme. The programme sets out the UK strategy for tackling climate change and includes specific measures related to the use of HFCs:
— HFCs should only be used where other safe, technically feasible, cost effective and more environmentally acceptable alternatives do not exist
— HFCs are not sustainable in the long term: the Government believes that continued technological developments will mean that HFCs may eventually be able to be replaced in the applications where they are used
— HFC emission reduction strategies should not undermine commitments to phase out ozone depleting substances under the Montreal Protocol
— HFC emissions will not be allowed to rise unchecked.
Alternative refrigerants such as hydrocarbons (HCs), CO2 and ammonia have lower global warming potential than HFCs but have other disadvantages such as high flammability or toxicity. The table below reproduced from F-gas Support summarises the refrigerant characteristics
Common Refrigerants
CFCs | HCFCs | HFCs | Other
R11 | R22 | R125 | R744 (CO2)
R12 | R403B | R134A | R717 (Ammonia)
| R408A | R404A | R290 (Propane)
| R123 | R407C | R600A (Isobutane)
R410A
R413A
R417A
Leakage testing frequency required under EC F gas Regulation

## Appendix C - Cooling Benchmarks
APPENDIX C Cooling Benchmarks
The estimate in TM44 Figure 4.1 Variation of calculated total heat gains with occupation density accounts for internal heat gains but the total cooling load may also have solar gain and ventilation loads
Therefore you can use TM44 figure 4.1 with and make a necessary allowance for solar and ventilation loads or you can use the benchmark data below from CIBSE guide F
Type of Building | Total Cooling Load W/m²
General Office | 125
Interior Zones | 75
Perimeter Zones (up to 6m)
- 65% glazing | 180
- 60% glazing | 120
Typical buildings:
- Retail | 140
- Banks | 160
- Restaurants | 220
- Hotels | 150-300
- Computer suites | 400 (approx.)
Office Type | Installed Refrigeration capacity (W/m²)
| Good Practice | Typical
Naturally Ventilated | 5 | 8
Air Conditioned Standard | 90 | 125
Air Conditioned Prestige | 100 | 135